Appendix – C2

Specification of Single Phase Electric Digital Meter
1.0 APPLICABLE STANDARDS 

The equipment and components supplied shall generally be in accordance with the latest editions/ amendments of the standards specified below following the relevant IEC Standard. However, the specific requirements mentioned below shall prevail.  

2.0 REQUIREMENTS

The meters to be supplied against this specification shall meet the requirements specified below.

2.1 Electrical requirements

Meter supplied shall meet the following electrical requirements.

	Sl. No
	Description
	Requirement

	1
	Connection
	1-phase, 2-wire, direct connected

	2
	Number of element
	2

	3
	Rated voltage
	230V phase to neutral 

	4
	Voltage Range
	 0.6  to 1.25 Un

	5
	Maximum withstand voltage 
	Should withstand 400 volts for one hour.

	6
	Base current, Ib
	5 A

	7
	Maximum continuous current, Imax
	60 A

	8
	Starting current
	20 mA (0.4% Ib)

	9
	Rated frequency
	50 Hz

	10
	Variation in frequency
	± 5%

	11
	Power factor
	Zero lag – unity – zero lead

	12
	Class index
	1.0

	13
	Power supply unit
	Preferably transformer less

	14
	Reference temperature 
	Reference temperature shall be 27oC. Mean temperature co-efficient should not exceed 0.07%.

	15
	Display 
	LCD

	16
	Period of display
	Continuous

	17
	Digits
	Width : 5 - 7  mm    Height : 7 - 10 mm

	18
	Maximum viewing angle
	160 degrees

	19
	Number of display digits
	SIX  (without decimal digit)

	20
	Display parameters
	Cumulative kWh

	21
	Power consumption at reference temperature, rated voltage and frequency
	 Shall not exceed 1 W and 8 VA in voltage circuit

Shall not exceed 1 VA in current circuit at base current

	22
	Harmonic energy
	Meter shall record total energy including harmonic energy

	23
	Memory
	Non volatile memory that retain information up to 10 years in the absence of power

	24
	Security features
	Should not be accessible for reprogramming at site

	25
	Display of Readings 
	Meter Reading shall be visible when Power is OFF or the Meter is disconnected by pressing a switch.

	26
	Battery
	Reputable and well-known manufacturers from USA / Japan / Germany / France / China or other EU countries.


2.2 Mechanical requirements

Meter supplied shall meet the following mechanical requirements.

	Sl. no.
	Description
	Requirement

	1
	Base & Cover
	Unbreakable, high grade, fire resistant, reinforced, UV stabilized polycarbonate. The meter cover shall be transparent.

	2
	Terminal cover
	Transparent, extended type; made of fire resistant, UV stabilized polycarbonate. The terminal cover shall have holes at the side for entry of the connecting wires.

	3
	Terminal block
	Polycarbonate grade 500R or equivalent bakelite; brass or copper current terminals; two flat-head brass screws (5-6 mm dia) at each terminal

	4
	Number of terminal
	4 (Four)

	5
	Minimum free space between bottom of terminal and terminal cover
	60 mm 

	6
	Minimum overall diameter of terminal hole inclusive of insulation thickness of service wire
	7 mm 

	7
	Connections diagrams and terminal marking
	Every meter shall be indelibly marked with a diagram of connection

Meter terminals shall be marked, this marking shall appear on the diagram .The line side terminal shall be located on the left & shall be labeled “Source” & load side terminal shall be located on the right & labeled “Load”.

	8
	Name plate
	Every meter shall have clearly visible, indelibly and distinctly marked name plate containing the following information:

Manufacturer’s name

Meter type

Number of phases and number of wire

Serial number and year of manufacture

Rated voltage of the system

Basic current and maximum current

Reference frequency in hertz

Meter constant in imp/kWh

Class index of the meter

	9
	Insulation level
	Shall withstand a power frequency voltage of 4 kV and impulse withstand test of 6 kV

	10
	Protection against penetration of dust and water 
	Conform to the degree of protection of IP 52

	11
	Resistance to heat and fire
	Terminal block and meter case shall have safety against spread of fire. Shall not be ignited by thermal overload of live parts in contact with them. Shall meet the tests stipulated in IEC 62053 or Equivalent.

	12
	Cover sealing 
	The meter main cover shall be ultrasonically welded so that once the meter is manufactured & tested at factory; it should not be possible to open.

	13
	Terminal cover sealing
	Sealable independently

	14
	Thickness of material for meter body 
	2 mm minimum for polycarbonate material 

	15
	Pulse output
	Flashing LED visible from the front.

	16
	Maximum pulse frequency
	Shall not exceed 2.5 kHz

	17
	Protection against magnetic field 
	Accuracy shall not be affected by AC/DC magnetic field of 0.2T on all the sides of meter. Meter working shall not be affected by permanent magnet of 0.5 T of minimum size 70x70x50 mm

	18
	Temperature range
	Specified operating range: -100C to 450C

Limit range of operation: -150C to 550C

Limit range of storage and transport: -200C to 700C


2.3 Component specifications

Components of the meter shall meet the following requirements.

	Sl. no.
	Component
	Requirement

	1
	Microcontroller
	Should be from reputed manufacturer with proven design.

Origin: Motorola, Xicor, Philips, Microchip, ST, Atmel, NEC, Oki, HOLTEC or equivalent reputable manufacturers with authentication of the proven standard quality. 

	2
	Measurement or computing chip
	Should be from reputed manufacturer with proven design.
Origin: Analog Devices, Cyrus Logic, Atmel, Philips, SAMES, NEC , TERIDIAN, Texas Instrument or equivalent reputable manufacturers with authentication of the proven standard quality.

	3
	Memory IC
	Should not be effected by external parameters like sparking, high voltage spikes or electrostatic discharges
Origin: Atmel, NS, TI, ST, Phillips, Hitachi, Oki, or equivalent reputable manufacturers with authentication of the proven standard quality.

	4
	Display modules
	i. Should be well protected from external UV radiations

ii. Visibility should be sufficient to read the meter mounted at height of 0.5 to 2.0 m

iii. Pin type

iv. Trans-reflective HTN or STN type industrial grade

v. Temperature range –200C to +700C.

Origin: Genda, Bonafide tecnologies, Advantek, Fordata, , Success, Hitachi, Sony , Smart Good , China display or equivalent reputable manufacturers with authentication of the proven standard quality..

	5
	PCB
	Glass epoxy, fire resistant grade FR4, minimum thickness 1.65 mm, finished copper thickness 1 oz/sft, lead free HAL surface treatment.


2.4 Tamper detection features

Meter accuracy shall not be affected in case of tamper condition. The meter shall detect and register correctly the energy only in forward direction under any or all tamper conditions. Visual indication shall be provided to show tamper condition.
	Sl. no
	Description
	Requirement

	1
	Remote control device
	Shall not get affected by any remote control device

	2
	Incoming and outgoing interchanged
	Should record forward energy

	3
	Phase and neutral interchanged
	Should record forward energy

	4
	Incoming neutral disconnected, outgoing neutral and load connected to earth
	Should record forward energy

	5
	Incoming neutral disconnected, outgoing neutral connected to earth through resistor and load connected to earth
	Should record forward energy

	6
	Incoming neutral connected, outgoing neutral connected to earth through resistor and load connected to earth
	Should record forward energy

	7
	Phase and neutral interchanged and load connected to earth 
	Should record forward energy

	8
	Incoming and outgoing (phase and neutral) interchanged, load connected to earth
	Should record forward energy

	9
	Incoming and outgoing (phase or neutral) interchanged, load connected to earth
	Should record forward energy

	10
	Incoming and outgoing (phase or neutral) interchanged, load connected to earth through resistor
	Should record forward energy


2.5 Electromagnetic compatibility

(a) Immunity to electromagnetic disturbance
The meter shall be designed in such a way that conducted or radiated electromagnetic disturbances as well as electrostatic discharge do not damage or substantially influence the meter. The disturbances to be considered are: 

i. Electrostatic discharges

ii. Electromagnetic HF field

iii. Fast transient burst

(b) Radio interference suppression 
The meters shall not generate conducted or radiated noise which could interfere with other equipment. 

2.6 Accuracy requirements 

(a) Limits of error due to variation of the current 
The percentage errors shall not exceed the limits for relevant accuracy class stipulated in IEC 62053-21 or Equivalent
(b) Limits of error due to other influence quantities 
The additional percentage error due to the change of influence quantities shall not exceed the limit for the reference accuracy class stipulated in IEC 62053-21 or Equivalent
 (c) Limits of error due to ambient temperature variation 
The limits of error shall not exceed the limits stipulated in IEC 62053-21 or Equivalent.
 (d) Starting and running with no-load 
Initial start-up of the meter: The meter shall be fully functional within 5 seconds after the voltage is applied to the meter terminals. 

Running with no load: When the voltage is applied with no current flowing in the current circuit the test output of the meter shall not produce more than one pulse. 

Starting: The meter shall start and continue to register at 0.4Ib% at power factor of 1. 

(e) Meter constant 
The relation between the test output and the indication in the display shall comply with the marking on the name-plate.
(f) Tamper Detection Features
The meter shall record forward energy accurately under the tamper detection features as mentioned in clause 4.4
3.0 Acceptance Test 

The following tests as per IEC 62053-21or Equivalent shall be witnessed by the representative(s) of the Purchaser. 
a) Tests of insulation properties 

i) AC Voltage Test 

b) Tests of accuracy requirements 

i) Test of meter constant 

ii) Test of starting condition 

iii) Test of no-load condition 

iv) Test of ambient temperature influence 

v) Test of influence quantities (only limits of error due to variation of the current)

c) Test of electrical requirements 

i) Test of power consumption 

d) Tamper Detection Requirements

Extra copies of the acceptance test report shall also be supplied with the meters. 

4.0 Routine Test 

Following routine tests as per IEC 62053-21 or Equivalent shall be carried out on all meters and each consignment of meters shall accompany one set of routine test results recorded in tabular form. If the test results are recorded in separate sheets all such sheets pertaining to each consignment shall be bound together as one volume. 
a) Tests of insulation properties 

i) AC Voltage Test 

b) Tests of accuracy requirements 

i) Test of meter constant 

ii) Test of starting condition 

iii) Test of no-load condition 

iv) Test of ambient temperature influence 

v) Test of influence quantities

c) Test of electrical requirements 

i) Test of power consumption 

ii) Test of influence of supply voltage

d) Test of mechanical requirements


i) Tests of protection against penetration of dust and water

Page 1 of 3

